## Background
Problem Description
The data table has four fields and shows monthly data for an elementary school in Chicago, IL. The only energy source is electricity.
Date: month shown as nominal first day (e.g. 1/1/2005 represents the month of January 2005). The relevant period is the school year, September through August.
kWh: kilowatt-hours usage for the month
Avg Monthly Mean Temp: National Weather Service monthly mean temperature in °F from NWS station at O'Hare International Airport
Heating Degree Days, Base 65 deg F: Calculation from NWS station
Practice Exercise:
Using the 24 months from Sept 2004 to August 2006, predict electricity use in the school year Sept 2007-Aug 2008.
Take a look at the school year Sept 2006-Aug 2007. The unusually low values for the winter are associated with broken air handling units, so we suggest omitting that school year from analysis.
Is there any evidence that electricity use has decreased in the school year Sept 2007-Aug 2008?
If so,
a) what is an estimate of dollar savings if the average 2007-2008 School year kWh cost was $0.08?
b) what is an estimate of environmental impact if each kWh is associated with 1.6 lbs of CO2 emissions?

## Data Table
Date | kwh | kwh(MMBTU) | Avg Monthly Mean Temp | Heating Degree Days, Base 65 deg F | Period
2004-09-01 | 75002 | 767.7524 | 66.5 | 47 | FY4
2004-10-01 | 78877.758 | 807.4263 | 53.9 | 338 | FY4
2004-11-01 | 84836.364 | 868.4212 | 43.7 | 632 | FY4
2004-12-01 | 145552.879 | 1489.9413 | 28.9 | 1113 | FY4
2005-01-01 | 169309.3 | 1733.1221 | 24.5 | 1248 | FY4
2005-02-01 | 122422.7 | 1253.1709 | 32.4 | 906 | FY4
2005-03-01 | 116321 | 1190.7113 | 35 | 926 | FY4
2005-04-01 | 78528.242 | 803.8485 | 51.5 | 401 | FY4
2005-05-01 | 71772.515 | 734.694 | 57.1 | 256 | FY4
2005-06-01 | 69332.309 | 709.7151 | 74.2 | 8 | FY4
2005-07-01 | 60156.496 | 615.7875 | 75.6 | 0 | FY4
2005-08-01 | 58740.334 | 601.2911 | 74.3 | 0 | FY4
2005-09-01 | 74584.069 | 763.4743 | 69.4 | 37 | FY5
2005-10-01 | 74307.731 | 760.6456 | 55.2 | 340 | FY5
2005-11-01 | 86853.206 | 889.0664 | 42 | 681 | FY5
2005-12-01 | 162894.784 | 1667.4604 | 23.3 | 1281 | FY5
2006-01-01 | 127338.313 | 1303.4892 | 35.8 | 896 | FY5
2006-02-01 | 135658.069 | 1388.6538 | 28.2 | 1024 | FY5
2006-03-01 | 121766.552 | 1246.4543 | 38.3 | 821 | FY5
2006-04-01 | 72690.067 | 744.0865 | 53.1 | 358 | FY5
2006-05-01 | 68997.106 | 706.2838 | 59.6 | 231 | FY5
2006-06-01 | 60499.94 | 619.3032 | 68.3 | 28 | FY5
2006-07-01 | 57798.331 | 591.6483 | 76.5 | 0 | FY5
2006-08-01 | 55055.435 | 563.5709 | 74.3 | 0 | FY5
2006-09-01 | 55335.672 | 566.4395 | 62.4 | 115 | FY6
2006-10-01 | 55653.918 | 569.6972 | 49 | 497 | FY6
2006-11-01 | 61117.366 | 625.6234 | 42.8 | 659 | FY6
2006-12-01 | 35998.086 | 368.4917 | 33.8 | 960 | FY6
2007-01-01 | 95477.224 | 977.3455 | 27.9 | 1141 | FY6
2007-02-01 | 108316.483 | 1108.7737 | 17.9 | 1310 | FY6
2007-03-01 | 78690.017 | 805.5045 | 42.5 | 697 | FY6
2007-04-01 | 61287.457 | 627.3645 | 46.8 | 543 | FY6
2007-05-01 | 72827.31 | 745.4914 | 63.8 | 116 | FY6
2007-06-01 | 71971.907 | 736.7351 | 71.3 | 18 | FY6
2007-07-01 | 51908.588 | 531.3584 | 73.7 | 0 | FY6
2007-08-01 | 53528.794 | 547.9435 | 74.8 | 1 | FY6
2007-09-01 | 68773.235 | 703.9921 | 68.1 | 56 | FY7
2007-10-01 | 70664.047 | 723.3473 | 59 | 234 | FY7
2007-11-01 | 85165.061 | 871.7858 | 39.4 | 763 | FY7
2007-12-01 | 127807.833 | 1308.2954 | 27.8 | 1146 | FY7
2008-01-01 | 146646.845 | 1501.1396 | 23.5 | 1280 | FY7
2008-02-01 | 137421.155 | 1406.7015 | 23 | 1211 | FY7
2008-03-01 | 118909.8103 | 1217.2115 | 34.9 | 926 | FY7
2008-04-01 | 90214.2069 | 923.4711 | 49.4 | 461 | FY7
2008-05-01 | 74594.7555 | 763.5837 | 55.5 | 290 | FY7
2008-06-01 | 55944.348 | 572.6702 | 70.8 | 4 | FY7
2008-07-01 | 51502.9248 | 527.2059 | 74 | 3 | FY7
2008-08-01 | 47462.4545 | 485.8459 | 72.7 | 0 | FY7

## 1 Detail Data (hidden)
Date | kwh | kwh(MMBTU) | Avg Monthly Mean Temp | Heating Degree Days, Base 65 deg F | Period | TOTAL (MMBtu) | Total Production | Baseline Year | Model Year | Period Count | Baseline Count | Energy Savings: kwh(MMBTU) | Energy Savings: TOTAL (MMBtu) | Unit Cost in $/MMBtu for column: kwh(MMBTU) | Unit Cost in $/MMBtu for column: TOTAL (MMBtu) | Cost Savings ($): kwh(MMBTU) | Cost Savings ($): TOTAL (MMBtu)
2004-09-01 | 75002 | 767.7524 | 66.5 | 47 | FY4 | 767.7524 | 617.6 | FY4 | 0 | 1 | 1 | 0 | 0 | 97.6903 |  | 0 | 0
2004-10-01 | 78877.758 | 807.4263 | 53.9 | 338 | FY4 | 807.4263 | 617.6 | FY4 | 0 | 2 | 2 | 0 | 0 | 97.6903 |  | 0 | 0
2004-11-01 | 84836.364 | 868.4212 | 43.7 | 632 | FY4 | 868.4212 | 617.6 | FY4 | 0 | 3 | 3 | 0 | 0 | 97.6903 |  | 0 | 0
2004-12-01 | 145552.879 | 1489.9413 | 28.9 | 1113 | FY4 | 1489.9413 | 617.6 | FY4 | 0 | 4 | 4 | 0 | 0 | 97.6903 |  | 0 | 0
2005-01-01 | 169309.3 | 1733.1221 | 24.5 | 1248 | FY4 | 1733.1221 | 617.6 | FY4 | 0 | 5 | 5 | 0 | 0 | 97.6903 |  | 0 | 0
2005-02-01 | 122422.7 | 1253.1709 | 32.4 | 906 | FY4 | 1253.1709 | 617.6 | FY4 | 0 | 6 | 6 | 0 | 0 | 97.6903 |  | 0 | 0
2005-03-01 | 116321 | 1190.7113 | 35 | 926 | FY4 | 1190.7113 | 617.6 | FY4 | 0 | 7 | 7 | 0 | 0 | 97.6903 |  | 0 | 0
2005-04-01 | 78528.242 | 803.8485 | 51.5 | 401 | FY4 | 803.8485 | 617.6 | FY4 | 0 | 8 | 8 | 0 | 0 | 97.6903 |  | 0 | 0
2005-05-01 | 71772.515 | 734.694 | 57.1 | 256 | FY4 | 734.694 | 617.6 | FY4 | 0 | 9 | 9 | 0 | 0 | 97.6903 |  | 0 | 0
2005-06-01 | 69332.309 | 709.7151 | 74.2 | 8 | FY4 | 709.7151 | 617.6 | FY4 | 0 | 10 | 10 | 0 | 0 | 97.6903 |  | 0 | 0
2005-07-01 | 60156.496 | 615.7875 | 75.6 | 0 | FY4 | 615.7875 | 617.6 | FY4 | 0 | 11 | 11 | 0 | 0 | 97.6903 |  | 0 | 0
2005-08-01 | 58740.334 | 601.2911 | 74.3 | 0 | FY4 | 601.2911 | 617.6 | FY4 | 0 | 12 | 12 | 0 | 0 | 97.6903 |  | 0 | 0
2005-09-01 | 74584.069 | 763.4743 | 69.4 | 37 | FY5 | 763.4743 | 624 | FY4 | 0 | 1 | 0 | 4.2781 | 4.2781 | 97.6903 |  | 417.931 | 0
2005-10-01 | 74307.731 | 760.6456 | 55.2 | 340 | FY5 | 760.6456 | 624 | FY4 | 0 | 2 | 0 | 46.7807 | 46.7807 | 97.6903 |  | 4570.027 | 0
2005-11-01 | 86853.206 | 889.0664 | 42 | 681 | FY5 | 889.0664 | 624 | FY4 | 0 | 3 | 0 | -20.6453 | -20.6453 | 97.6903 |  | -2016.842 | 0
2005-12-01 | 162894.784 | 1667.4604 | 23.3 | 1281 | FY5 | 1667.4604 | 624 | FY4 | 0 | 4 | 0 | -177.5191 | -177.5191 | 97.6903 |  | -17341.905 | 0
2006-01-01 | 127338.313 | 1303.4892 | 35.8 | 896 | FY5 | 1303.4892 | 624 | FY4 | 0 | 5 | 0 | 429.6329 | 429.6329 | 97.6903 |  | 41970.987 | 0
2006-02-01 | 135658.069 | 1388.6538 | 28.2 | 1024 | FY5 | 1388.6538 | 624 | FY4 | 0 | 6 | 0 | -135.4829 | -135.4829 | 97.6903 |  | -13235.369 | 0
2006-03-01 | 121766.552 | 1246.4543 | 38.3 | 821 | FY5 | 1246.4543 | 624 | FY4 | 0 | 7 | 0 | -55.743 | -55.743 | 97.6903 |  | -5445.552 | 0
2006-04-01 | 72690.067 | 744.0865 | 53.1 | 358 | FY5 | 744.0865 | 624 | FY4 | 0 | 8 | 0 | 59.762 | 59.762 | 97.6903 |  | 5838.175 | 0
2006-05-01 | 68997.106 | 706.2838 | 59.6 | 231 | FY5 | 706.2838 | 624 | FY4 | 0 | 9 | 0 | 28.4103 | 28.4103 | 97.6903 |  | 2775.409 | 0
2006-06-01 | 60499.94 | 619.3032 | 68.3 | 28 | FY5 | 619.3032 | 624 | FY4 | 0 | 10 | 0 | 90.4119 | 90.4119 | 97.6903 |  | 8832.369 | 0
2006-07-01 | 57798.331 | 591.6483 | 76.5 | 0 | FY5 | 591.6483 | 624 | FY4 | 0 | 11 | 0 | 24.1392 | 24.1392 | 97.6903 |  | 2358.165 | 0
2006-08-01 | 55055.435 | 563.5709 | 74.3 | 0 | FY5 | 563.5709 | 624 | FY4 | 0 | 12 | 0 | 37.7202 | 37.7202 | 97.6903 |  | 3684.899 | 0
2006-09-01 | 55335.672 | 566.4395 | 62.4 | 115 | FY6 | 566.4395 | 606.7 | FY4 | 0 | 1 | 0 | 201.3129 | 201.3129 | 97.6903 |  | 19666.328 | 0
2006-10-01 | 55653.918 | 569.6972 | 49 | 497 | FY6 | 569.6972 | 606.7 | FY4 | 0 | 2 | 0 | 237.7291 | 237.7291 | 97.6903 |  | 23223.84 | 0
2006-11-01 | 61117.366 | 625.6234 | 42.8 | 659 | FY6 | 625.6234 | 606.7 | FY4 | 0 | 3 | 0 | 242.7978 | 242.7978 | 97.6903 |  | 23718.998 | 0
2006-12-01 | 35998.086 | 368.4917 | 33.8 | 960 | FY6 | 368.4917 | 606.7 | FY4 | 0 | 4 | 0 | 1121.4495 | 1121.4495 | 97.6903 |  | 109554.793 | 0
2007-01-01 | 95477.224 | 977.3455 | 27.9 | 1141 | FY6 | 977.3455 | 606.7 | FY4 | 0 | 5 | 0 | 755.7766 | 755.7766 | 97.6903 |  | 73832.076 | 0
2007-02-01 | 108316.483 | 1108.7737 | 17.9 | 1310 | FY6 | 1108.7737 | 606.7 | FY4 | 0 | 6 | 0 | 144.3972 | 144.3972 | 97.6903 |  | 14106.217 | 0
2007-03-01 | 78690.017 | 805.5045 | 42.5 | 697 | FY6 | 805.5045 | 606.7 | FY4 | 0 | 7 | 0 | 385.2068 | 385.2068 | 97.6903 |  | 37630.983 | 0
2007-04-01 | 61287.457 | 627.3645 | 46.8 | 543 | FY6 | 627.3645 | 606.7 | FY4 | 0 | 8 | 0 | 176.484 | 176.484 | 97.6903 |  | 17240.785 | 0
2007-05-01 | 72827.31 | 745.4914 | 63.8 | 116 | FY6 | 745.4914 | 606.7 | FY4 | 0 | 9 | 0 | -10.7973 | -10.7973 | 97.6903 |  | -1054.795 | 0
2007-06-01 | 71971.907 | 736.7351 | 71.3 | 18 | FY6 | 736.7351 | 606.7 | FY4 | 0 | 10 | 0 | -27.02 | -27.02 | 97.6903 |  | -2639.598 | 0
2007-07-01 | 51908.588 | 531.3584 | 73.7 | 0 | FY6 | 531.3584 | 606.7 | FY4 | 0 | 11 | 0 | 84.4291 | 84.4291 | 97.6903 |  | 8247.908 | 0
2007-08-01 | 53528.794 | 547.9435 | 74.8 | 1 | FY6 | 547.9435 | 606.7 | FY4 | 0 | 12 | 0 | 53.3475 | 53.3475 | 97.6903 |  | 5211.54 | 0
2007-09-01 | 68773.235 | 703.9921 | 68.1 | 56 | FY7 | 703.9921 | 598.1 | FY4 | 0 | 1 | 0 | 63.7603 | 63.7603 | 97.6903 |  | 6228.765 | 0
2007-10-01 | 70664.047 | 723.3473 | 59 | 234 | FY7 | 723.3473 | 598.1 | FY4 | 0 | 2 | 0 | 84.079 | 84.079 | 97.6903 |  | 8213.711 | 0
2007-11-01 | 85165.061 | 871.7858 | 39.4 | 763 | FY7 | 871.7858 | 598.1 | FY4 | 0 | 3 | 0 | -3.3647 | -3.3647 | 97.6903 |  | -328.697 | 0
2007-12-01 | 127807.833 | 1308.2954 | 27.8 | 1146 | FY7 | 1308.2954 | 598.1 | FY4 | 0 | 4 | 0 | 181.6459 | 181.6459 | 97.6903 |  | 17745.046 | 0
2008-01-01 | 146646.845 | 1501.1396 | 23.5 | 1280 | FY7 | 1501.1396 | 598.1 | FY4 | 0 | 5 | 0 | 231.9825 | 231.9825 | 97.6903 |  | 22662.455 | 0
2008-02-01 | 137421.155 | 1406.7015 | 23 | 1211 | FY7 | 1406.7015 | 598.1 | FY4 | 0 | 6 | 0 | -153.5306 | -153.5306 | 97.6903 |  | -14998.455 | 0
2008-03-01 | 118909.8103 | 1217.2115 | 34.9 | 926 | FY7 | 1217.2115 | 598.1 | FY4 | 0 | 7 | 0 | -26.5002 | -26.5002 | 97.6903 |  | -2588.8103 | 0
2008-04-01 | 90214.2069 | 923.4711 | 49.4 | 461 | FY7 | 923.4711 | 598.1 | FY4 | 0 | 8 | 0 | -119.6225 | -119.6225 | 97.6903 |  | -11685.9649 | 0
2008-05-01 | 74594.7555 | 763.5837 | 55.5 | 290 | FY7 | 763.5837 | 598.1 | FY4 | 0 | 9 | 0 | -28.8897 | -28.8897 | 97.6903 |  | -2822.2405 | 0
2008-06-01 | 55944.348 | 572.6702 | 70.8 | 4 | FY7 | 572.6702 | 598.1 | FY4 | 0 | 10 | 0 | 137.0449 | 137.0449 | 97.6903 |  | 13387.961 | 0
2008-07-01 | 51502.9248 | 527.2059 | 74 | 3 | FY7 | 527.2059 | 598.1 | FY4 | 0 | 11 | 0 | 88.5816 | 88.5816 | 97.6903 |  | 8653.5712 | 0
2008-08-01 | 47462.4545 | 485.8459 | 72.7 | 0 | FY7 | 485.8459 | 598.1 | FY4 | 0 | 12 | 0 | 115.4452 | 115.4452 | 97.6903 |  | 11277.8795 | 0
Data Table

## 1 EnPI Actual Results
General Energy Performance Results
| FY4 | FY5 | FY6 | FY7
kwh(MMBTU) | 11575.8818 | 11244.1367 | 8210.7685 | 11005.2499
TOTAL (MMBtu) | 11575.8818 | 11244.1367 | 8210.7685 | 11005.2499
kwh(MMBTU) Annual Savings | 0 | 331.7451 | 3365.1132 | 570.6318
kwh(MMBTU) Estimated Cost Savings ($) | 0 | 32408.294 | 328739.075 | 55745.221
Total Production Output | 617.6 | 624 | 606.7 | 598.1
Production Energy Intensity (MMBtu/unit production) | 18.7433 | 18.0194 | 13.5335 | 18.4004
Total Improvement in Energy Intensity (%) | 0% | 3.862% | 27.8% | 1.83%
Annual Improvement in Energy Intensity (%) | 0% | 3.862% | 23.93% | -25.97%
Total Savings Since Baseline Year (MMBtu/Year) | 0 | 331.7451 | 3365.1132 | 570.6318
New Energy Savings for Current Year (MMBtu/year) | 0 | 331.7451 | 3033.3681 | -2794.4814
Estimated Annual Cost Savings | 0 | 32408.294 | 328739.075 | 55745.221
Avoided CO2 Emissions (Metric Ton/year) | 0 | 82.5813 | 837.6776 | 142.0474

## 2 kwh(MMBTU)
The best model for the data provided is #1
2 kwh(MMBTU) Models
The table below shows all possible models for 2 kwh(MMBTU) consumption. The model highlighted in green in the table below is the model with the highest Adjusted R2 value. If "true" is shown in column B, the model is designated as valid. A model is considered valid if the model p-value is less than 0.10. The model highlighted in green is used to calculate the adjusted data on the EnPI Results, SEnPI Results, and Adjusted Data tabs. If the model is switched, the corresponding data will be updated with the model selected. The models can be switched using the "Change Models" icon in the top navigation.
Model Number | Model is Appropriate for SEP | Variables | Coefficients | Variable Std. Error | Variable p-Values | R2 | Adjusted R2 | Model p-Value | RMSError | Residual | AIC | Formula
1 | TRUE | Heating Degree Days, Base 65 deg F | 0.75443 | 0.077027 | 1.9224e-06 | 0.9056 | 0.89616 | 1.9224e-06 | 107.5754 | 138869.6264 |  | (0.754431583882666 * [Heating Degree Days, Base 65 deg F]) + 595.299683774121
595.2997
The plots below show the actual energy consumption versus the independent variables for the model year. | [5 empty] | The line labeled "Actuals" in the plot below has not been adjusted. This is the original data entered by the user. The line labeled "Model" is the predicted energy consumption using the model selected above.

## stateData (hidden)
Column1 | Column2 | Column3 | Column4 | Column1 | Column2 | Column3 | Column4
e69d856d-5a70-4c66-b887-9d85a370ca9a | 1 Detail Data | FALSE | TRUE | 570acbf2-ad05-4f55-a3dd-27b6ca00866d | 2 kwh(MMBTU) | FALSE | FALSE
0b200520-1dab-452d-aa40-f2b74469fcc0 | 1 EnPI Actual Results | TRUE | FALSE | be6eeefd-2812-43c8-bf13-cc06323c1e0c | 2 Model Data | FALSE | TRUE
regressionIteration | 1 |  |  | e001857e-38b3-4886-8570-667f48222d42 | 2 EnPI Results | TRUE | FALSE
plantName | Data Table |  |  | 181843b4-ef9c-4fca-a158-d2294a3bce36 | 2 SEnPIResults | TRUE | FALSE
|  |  |  | regressionIteration | 2
|  |  |  | plantName | Data Table

## 2 Model Data
Negative Values
One or more of the calculated modeled energy consumption values is negative. The negative modeled energy value(s) is shown in yellow. Consider setting the negative modeled energy value as zero.
Validation Check
A model must satisfy validity requirements in order to be used for SEP or Better Plants reporting. In addition to the model having acceptable R-squared and p-values, the average of the variables entered into the model must fall within one of the following ranges: 1. The range of observed data that went into the model OR 2. Three standard deviations from the mean of the data that went into the model The following table shows these ranges for the data set provided.
Column1 | Column2 | Heating Degree Days, Base 65 deg F
Range 1 | Minimum of Model Variable
Maximum of Model Variable
Range 2 | Model Avg -3 Std Dev
Model Avg +3 Std Dev
Date | kwh | kwh(MMBTU) | Avg Monthly Mean Temp | Heating Degree Days, Base 65 deg F | Period | TOTAL (MMBtu) | Total Production | Baseline Year | Model Year | Last Year | Adjustment Method | Modeled kwh(MMBTU) | Total Modeled Energy Consumption (MMBtu) | CUSUMHidden | SEP CUSUM | Energy Savings: kwh(MMBTU) | Unit Cost in $/MMBtu for column: kwh(MMBTU) | Cost Savings ($): kwh(MMBTU)
2004-09-01 | 75002 | 767.7524 | 66.5 | 47 | FY4 | 767.7524 | 617.6 | FY4 | FY4 | FY7 | Model Year | 630.758 | 630.758 | 0 |  | -136.9945 | 97.6903 | -13383.0357
2004-10-01 | 78877.758 | 807.4263 | 53.9 | 338 | FY4 | 807.4263 | 617.6 | FY4 | FY4 | FY7 | Model Year | 850.2976 | 850.2976 | 0 |  | 42.8712 | 97.6903 | 4188.1049
2004-11-01 | 84836.364 | 868.4212 | 43.7 | 632 | FY4 | 868.4212 | 617.6 | FY4 | FY4 | FY7 | Model Year | 1072.1004 | 1072.1004 | 0 |  | 203.6793 | 97.6903 | 19897.4996
2004-12-01 | 145552.879 | 1489.9413 | 28.9 | 1113 | FY4 | 1489.9413 | 617.6 | FY4 | FY4 | FY7 | Model Year | 1434.982 | 1434.982 | 0 |  | -54.9592 | 97.6903 | -5368.987
2005-01-01 | 169309.3 | 1733.1221 | 24.5 | 1248 | FY4 | 1733.1221 | 617.6 | FY4 | FY4 | FY7 | Model Year | 1536.8303 | 1536.8303 | 0 |  | -196.2918 | 97.6903 | -19175.8159
2005-02-01 | 122422.7 | 1253.1709 | 32.4 | 906 | FY4 | 1253.1709 | 617.6 | FY4 | FY4 | FY7 | Model Year | 1278.8147 | 1278.8147 | 0 |  | 25.6438 | 97.6903 | 2505.1507
2005-03-01 | 116321 | 1190.7113 | 35 | 926 | FY4 | 1190.7113 | 617.6 | FY4 | FY4 | FY7 | Model Year | 1293.9033 | 1293.9033 | 0 |  | 103.192 | 97.6903 | 10080.8643
2005-04-01 | 78528.242 | 803.8485 | 51.5 | 401 | FY4 | 803.8485 | 617.6 | FY4 | FY4 | FY7 | Model Year | 897.8267 | 897.8267 | 0 |  | 93.9782 | 97.6903 | 9180.7639
2005-05-01 | 71772.515 | 734.694 | 57.1 | 256 | FY4 | 734.694 | 617.6 | FY4 | FY4 | FY7 | Model Year | 788.4342 | 788.4342 | 0 |  | 53.7401 | 97.6903 | 5249.892
2005-06-01 | 69332.309 | 709.7151 | 74.2 | 8 | FY4 | 709.7151 | 617.6 | FY4 | FY4 | FY7 | Model Year | 601.3351 | 601.3351 | 0 |  | -108.3799 | 97.6903 | -10587.6713
2005-07-01 | 60156.496 | 615.7875 | 75.6 | 0 | FY4 | 615.7875 | 617.6 | FY4 | FY4 | FY7 | Model Year | 595.2997 | 595.2997 | 0 |  | -20.4878 | 97.6903 | -2001.4638
2005-08-01 | 58740.334 | 601.2911 | 74.3 | 0 | FY4 | 601.2911 | 617.6 | FY4 | FY4 | FY7 | Model Year | 595.2997 | 595.2997 | 0 |  | -5.9914 | 97.6903 | -585.3018
2005-09-01 | 74584.069 | 763.4743 | 69.4 | 37 | FY5 | 763.4743 | 624 | FY4 | FY4 | FY7 | Forecast | 623.2137 | 623.2137 | 140.2607 | 140.2607 | -140.2607 | 97.6903 | -13702.1115
2005-10-01 | 74307.731 | 760.6456 | 55.2 | 340 | FY5 | 760.6456 | 624 | FY4 | FY4 | FY7 | Forecast | 851.8064 | 851.8064 | 49.0998 | 49.0998 | 91.1608 | 97.6903 | 8905.5333
2005-11-01 | 86853.206 | 889.0664 | 42 | 681 | FY5 | 889.0664 | 624 | FY4 | FY4 | FY7 | Forecast | 1109.0676 | 1109.0676 | -170.9014 | -170.9014 | 220.0012 | 97.6903 | 21491.9911
2005-12-01 | 162894.784 | 1667.4604 | 23.3 | 1281 | FY5 | 1667.4604 | 624 | FY4 | FY4 | FY7 | Forecast | 1561.7265 | 1561.7265 | -65.1675 | -65.1675 | -105.7339 | 97.6903 | -10329.1773
2006-01-01 | 127338.313 | 1303.4892 | 35.8 | 896 | FY5 | 1303.4892 | 624 | FY4 | FY4 | FY7 | Forecast | 1271.2704 | 1271.2704 | -32.9487 | -32.9487 | -32.2188 | 97.6903 | -3147.4692
2006-02-01 | 135658.069 | 1388.6538 | 28.2 | 1024 | FY5 | 1388.6538 | 624 | FY4 | FY4 | FY7 | Forecast | 1367.8376 | 1367.8376 | -12.1325 | -12.1325 | -20.8162 | 97.6903 | -2033.5378
2006-03-01 | 121766.552 | 1246.4543 | 38.3 | 821 | FY5 | 1246.4543 | 624 | FY4 | FY4 | FY7 | Forecast | 1214.688 | 1214.688 | 19.6338 | 19.6338 | -31.7663 | 97.6903 | -3103.2593
2006-04-01 | 72690.067 | 744.0865 | 53.1 | 358 | FY5 | 744.0865 | 624 | FY4 | FY4 | FY7 | Forecast | 865.3862 | 865.3862 | -101.6659 | -101.6659 | 121.2997 | 97.6903 | 11849.8096
2006-05-01 | 68997.106 | 706.2838 | 59.6 | 231 | FY5 | 706.2838 | 624 | FY4 | FY4 | FY7 | Forecast | 769.5734 | 769.5734 | -164.9555 | -164.9555 | 63.2896 | 97.6903 | 6182.7839
2006-06-01 | 60499.94 | 619.3032 | 68.3 | 28 | FY5 | 619.3032 | 624 | FY4 | FY4 | FY7 | Forecast | 616.4238 | 616.4238 | -162.0761 | -162.0761 | -2.8794 | 97.6903 | -281.2887
2006-07-01 | 57798.331 | 591.6483 | 76.5 | 0 | FY5 | 591.6483 | 624 | FY4 | FY4 | FY7 | Forecast | 595.2997 | 595.2997 | -165.7275 | -165.7275 | 3.6513 | 97.6903 | 356.7012
2006-08-01 | 55055.435 | 563.5709 | 74.3 | 0 | FY5 | 563.5709 | 624 | FY4 | FY4 | FY7 | Forecast | 595.2997 | 595.2997 | -197.4563 | -197.4563 | 31.7288 | 97.6903 | 3099.5972
2006-09-01 | 55335.672 | 566.4395 | 62.4 | 115 | FY6 | 566.4395 | 606.7 | FY4 | FY4 | FY7 | Forecast | 682.0593 | 682.0593 | -313.0761 | -313.0761 | 115.6198 | 97.6903 | 11294.9387
2006-10-01 | 55653.918 | 569.6972 | 49 | 497 | FY6 | 569.6972 | 606.7 | FY4 | FY4 | FY7 | Forecast | 970.2522 | 970.2522 | -713.6311 | -713.6311 | 400.555 | 97.6903 | 39130.3535
2006-11-01 | 61117.366 | 625.6234 | 42.8 | 659 | FY6 | 625.6234 | 606.7 | FY4 | FY4 | FY7 | Forecast | 1092.4701 | 1092.4701 | -1180.4778 | -1180.4778 | 466.8467 | 97.6903 | 45606.4161
2006-12-01 | 35998.086 | 368.4917 | 33.8 | 960 | FY6 | 368.4917 | 606.7 | FY4 | FY4 | FY7 | Forecast | 1319.554 | 1319.554 | -2131.54 | -2131.54 | 951.0623 | 97.6903 | 92909.6015
2007-01-01 | 95477.224 | 977.3455 | 27.9 | 1141 | FY6 | 977.3455 | 606.7 | FY4 | FY4 | FY7 | Forecast | 1456.1061 | 1456.1061 | -2610.3006 | -2610.3006 | 478.7606 | 97.6903 | 46770.2871
2007-02-01 | 108316.483 | 1108.7737 | 17.9 | 1310 | FY6 | 1108.7737 | 606.7 | FY4 | FY4 | FY7 | Forecast | 1583.6051 | 1583.6051 | -3085.132 | -3085.132 | 474.8314 | 97.6903 | 46386.4435
2007-03-01 | 78690.017 | 805.5045 | 42.5 | 697 | FY6 | 805.5045 | 606.7 | FY4 | FY4 | FY7 | Forecast | 1121.1385 | 1121.1385 | -3400.766 | -3400.766 | 315.634 | 97.6903 | 30834.391
2007-04-01 | 61287.457 | 627.3645 | 46.8 | 543 | FY6 | 627.3645 | 606.7 | FY4 | FY4 | FY7 | Forecast | 1004.956 | 1004.956 | -3778.3575 | -3778.3575 | 377.5915 | 97.6903 | 36887.0459
2007-05-01 | 72827.31 | 745.4914 | 63.8 | 116 | FY6 | 745.4914 | 606.7 | FY4 | FY4 | FY7 | Forecast | 682.8137 | 682.8137 | -3715.6799 | -3715.6799 | -62.6776 | 97.6903 | -6122.9986
2007-06-01 | 71971.907 | 736.7351 | 71.3 | 18 | FY6 | 736.7351 | 606.7 | FY4 | FY4 | FY7 | Forecast | 608.8795 | 608.8795 | -3587.8242 | -3587.8242 | -127.8556 | 97.6903 | -12490.2625
2007-07-01 | 51908.588 | 531.3584 | 73.7 | 0 | FY6 | 531.3584 | 606.7 | FY4 | FY4 | FY7 | Forecast | 595.2997 | 595.2997 | -3651.7655 | -3651.7655 | 63.9413 | 97.6903 | 6246.4442
2007-08-01 | 53528.794 | 547.9435 | 74.8 | 1 | FY6 | 547.9435 | 606.7 | FY4 | FY4 | FY7 | Forecast | 596.0541 | 596.0541 | -3699.876 | -3699.876 | 48.1106 | 97.6903 | 4699.9389
2007-09-01 | 68773.235 | 703.9921 | 68.1 | 56 | FY7 | 703.9921 | 598.1 | FY4 | FY4 | FY7 | Forecast | 637.5479 | 637.5479 | -3633.4318 | -3633.4318 | -66.4443 | 97.6903 | -6490.9646
2007-10-01 | 70664.047 | 723.3473 | 59 | 234 | FY7 | 723.3473 | 598.1 | FY4 | FY4 | FY7 | Forecast | 771.8367 | 771.8367 | -3681.9212 | -3681.9212 | 48.4894 | 97.6903 | 4736.9449
2007-11-01 | 85165.061 | 871.7858 | 39.4 | 763 | FY7 | 871.7858 | 598.1 | FY4 | FY4 | FY7 | Forecast | 1170.931 | 1170.931 | -3981.0663 | -3981.0663 | 299.1451 | 97.6903 | 29223.5921
2007-12-01 | 127807.833 | 1308.2954 | 27.8 | 1146 | FY7 | 1308.2954 | 598.1 | FY4 | FY4 | FY7 | Forecast | 1459.8783 | 1459.8783 | -4132.6491 | -4132.6491 | 151.5829 | 97.6903 | 14808.1815
2008-01-01 | 146646.845 | 1501.1396 | 23.5 | 1280 | FY7 | 1501.1396 | 598.1 | FY4 | FY4 | FY7 | Forecast | 1560.9721 | 1560.9721 | -4192.4817 | -4192.4817 | 59.8325 | 97.6903 | 5845.061
2008-02-01 | 137421.155 | 1406.7015 | 23 | 1211 | FY7 | 1406.7015 | 598.1 | FY4 | FY4 | FY7 | Forecast | 1508.9163 | 1508.9163 | -4294.6965 | -4294.6965 | 102.2148 | 97.6903 | 9985.4039
2008-03-01 | 118909.8103 | 1217.2115 | 34.9 | 926 | FY7 | 1217.2115 | 598.1 | FY4 | FY4 | FY7 | Forecast | 1293.9033 | 1293.9033 | -4371.3884 | -4371.3884 | 76.6919 | 97.6903 | 7492.054
2008-04-01 | 90214.2069 | 923.4711 | 49.4 | 461 | FY7 | 923.4711 | 598.1 | FY4 | FY4 | FY7 | Forecast | 943.0926 | 943.0926 | -4391.01 | -4391.01 | 19.6216 | 97.6903 | 1916.84
2008-05-01 | 74594.7555 | 763.5837 | 55.5 | 290 | FY7 | 763.5837 | 598.1 | FY4 | FY4 | FY7 | Forecast | 814.0848 | 814.0848 | -4441.5111 | -4441.5111 | 50.5011 | 97.6903 | 4933.4747
2008-06-01 | 55944.348 | 572.6702 | 70.8 | 4 | FY7 | 572.6702 | 598.1 | FY4 | FY4 | FY7 | Forecast | 598.3174 | 598.3174 | -4467.1584 | -4467.1584 | 25.6472 | 97.6903 | 2505.487
2008-07-01 | 51502.9248 | 527.2059 | 74 | 3 | FY7 | 527.2059 | 598.1 | FY4 | FY4 | FY7 | Forecast | 597.563 | 597.563 | -4537.5155 | -4537.5155 | 70.3571 | 97.6903 | 6873.2095
2008-08-01 | 47462.4545 | 485.8459 | 72.7 | 0 | FY7 | 485.8459 | 598.1 | FY4 | FY4 | FY7 | Forecast | 595.2997 | 595.2997 | -4646.9692 | -4646.9692 | 109.4538 | 97.6903 | 10692.5777
Data Table Original and Modeled Values The table below shows the energy and independent variable data originally entered in the tool, the adjusted data, adjustment method, and totals. The data used for the model year is highlighted in green. If a new model is selected for an individual energy source, the adjusted values below will be updated. The EnPI/SEnPI results pages are also linked to this page. Therefore, if changes are made to the adjusted data in the columns below, the results shown in the EnPI and SEnPI pages will update. However, this data is not linked to the orginal source data, so changes made to this page will not affect the data originally entered.

## 2 EnPI Results
General Energy Performance Results
The table below shows the unadjusted and adjusted energy consumption and intensity data. The models used to adjust the data for each energy source are shown below the plots and on the individual sheets for each energy source. Note that the tool selects the model that is appropriate for the SEP Program and has the highest adjusted R-squared value.
| FY4 | FY5 | FY6 | FY7
Actual kwh(MMBTU) | 11575.8818 | 11244.1367 | 8210.7685 | 11005.2499
TOTAL (MMBtu) | 11575.8818 | 11244.1367 | 8210.7685 | 11005.2499
Adjustment Method | Model Year | Forecast | Forecast | Forecast
Modeled kwh(MMBTU) | 11575.8818 | 11441.5929 | 11713.1883 | 11952.3431
kwh(MMBTU) Annual Savings | 0 | 197.4563 | 3502.4198 | 947.0932
kwh(MMBTU) Estimated Cost Savings ($) | -6.1141e-10 | 19289.5725 | 342152.5992 | 92521.8616
Total Modeled Energy Consumption (MMBtu) | 11575.8818 | 11441.5929 | 11713.1883 | 11952.3431
SEnPI Cumulative | 1 | 0.98274 | 0.70098 | 0.92076
Total Improvement in Energy Intensity (%) | 0% | 1.726% | 29.9% | 7.924%
Annual Improvement in Energy Intensity (%) | 0% | 1.726% | 28.18% | -21.98%
Total Energy Savings since Baseline Year (MMBtu/Year) | 0 | 197.4563 | 3502.4198 | 947.0932
Cumulative Savings (MMBtu) | 0 | 197.4563 | 3699.876 | 4646.9692
New Energy Savings for Current Year (MMBtu/year) | 0 | 197.4563 | 3304.9635 | -2555.3266
Adjustment for Baseline Primary Energy Use (MMBtu/year) | 0 | -134.2888 | 137.3065 | 376.4614
Estimated Annual Cost Savings | -6.1141e-10 | 19289.5725 | 342152.5992 | 92521.8616
Avoided CO2 Emissions (Metric Ton/year) | 0 | 45.8671 | 813.5771 | 220.0003
Warnings
Energy Use | Model is Appropriate for SEP | Variables | Variable p-Values | R2 | Adjusted R2 | Model p-Value | Formula
2 kwh(MMBTU) | TRUE | Heating Degree Days, Base 65 deg F | 1.9224e-06 | 0.9056 | 0.89616 | 1.9224e-06 | (0.754431583882666 * [Heating Degree Days, Base 65 deg F]) + 595.299683774121

## 2 SEnPIResults
Superior Energy Performance Results
The table below shows the unadjusted and adjusted energy consumption and intensity data. The models used to adjust the data for each energy source are shown below the plots and on the individual sheets for each energy source. Note that the tool selects the model that is appropriate for the SEP Program and has the highest adjusted R-squared value.
| FY4 | FY5 | FY6 | FY7
Actual kwh(MMBTU) | 11575.8818 | 11244.1367 | 8210.7685 | 11005.2499
TOTAL (MMBtu) | 11575.8818 | 11244.1367 | 8210.7685 | 11005.2499
Adjustment Method | Model Year | Forecast | Forecast | Forecast
Modeled kwh(MMBTU) | 11575.8818 | 11441.5929 | 11713.1883 | 11952.3431
kwh(MMBTU) Annual Savings | 0 | 197.4563 | 3502.4198 | 947.0932
kwh(MMBTU) Estimated Cost Savings ($) | -6.1141e-10 | 19289.5725 | 342152.5992 | 92521.8616
Total Modeled Energy Consumption (MMBtu) | 11575.8818 | 11441.5929 | 11713.1883 | 11952.3431
SEnPI Cumulative | 1 | 0.98274 | 0.70098 | 0.92076
Cumulative Improvement (%) | 0% | 1.726% | 29.9% | 7.924%
Annual Improvement (%) | 0% | 1.726% | 28.18% | -21.98%
Annual Savings (MMBtu/year) | 0 | 197.4563 | 3502.4198 | 947.0932
Cumulative Savings (MMBtu) | 0 | 197.4563 | 3699.876 | 4646.9692
New Energy Savings for Current Year (MMBtu/year) | 0 | 197.4563 | 3304.9635 | -2555.3266
Adjustment for Baseline Primary Energy Use (MMBtu/year) | 0 | -134.2888 | 137.3065 | 376.4614
Estimated Annual Cost Savings | -6.1141e-10 | 19289.5725 | 342152.5992 | 92521.8616
Avoided CO2 Emissions (Metric Ton/year) | 0 | 45.8671 | 813.5771 | 220.0003
Warnings
Energy Use | Model is Appropriate for SEP | Variables | Variable p-Values | R2 | Adjusted R2 | Model p-Value | Formula
2 kwh(MMBTU) | TRUE | Heating Degree Days, Base 65 deg F | 1.9224e-06 | 0.9056 | 0.89616 | 1.9224e-06 | (0.754431583882666 * [Heating Degree Days, Base 65 deg F]) + 595.299683774121